DRAFT MAINTENANCE - ARCHITECTURAL INTERIOR PUNCH LIST

Date Conducted	2019.01.16

Architect:	BSW

By:	DAchterberg, CCollins, KPhillips, JRonson, CMeredeth, JRichards

Job No.:	21607

GENERAL NOTES:	1.)

2.)

3.)

4.)

5.)

Ensure all imperfections marked by painter's tape during walk-through have been corrected.

Ensure all lock cores have been changed from master cores; all electronic locks have been programmed to Owner requirements.

At final clean replace all damaged ceiling tiles.

Schedule Owner training.

|  | Room No./ Name | 3001 VEHICLES |
| --- | --- | --- |
|  | ITEM | APP | REJ | COMMENTS |
|  | North Wall |  |  |  |
|  | South Wall |  |  |  |
|  |  |  |  | Attach electrical conduit to wall from unit over door. Seal around exterior vent duct. Door 3001B: Seal around new door, remove existing abandoned |
|  | East Wall |  |  | conduit to the right side of door, caulk hole with black cable through walll, near floor, right of door. |
|  | West Wall |  |  |  |
|  | Flooring |  |  |  |
|  | Base |  |  |  |
|  | Doors |  |  | Door 3001A to self close and latch (fire). |
|  | Ceiling |  |  |  |
|  | Lighting |  |  |  |
|  | Power |  |  |  |
|  | HVAC |  |  | Install conduit and thermostat in wall, not surface mounted. |
|  | Millwork |  |  | Infill minor gaps in plywood on wall at tops. |
|  | Plumbing |  |  |  |
|  | Other |  |  | Seal all existing abandoned floor drains by removing covers and filling with concrete flush to floor. |
|  | Other |  |  |  |

|  | Room No./ Name | 3003 WORK |
| --- | --- | --- |
|  | ITEM | APP | REJ | COMMENTS |
|  | North Wall |  |  |  |
|  | South Wall |  |  | Fill in existing recess for former garage door along new wall flush to floor. |
|  | East Wall |  |  |  |
|  | West Wall |  |  |  |
|  | Flooring |  |  |  |
|  | Base |  |  |  |
|  | Doors |  |  | Adjust door closer on door 3003A |
|  | Ceiling |  |  |  |
|  | Lighting |  |  | Remove tie (?) wire at ceiling fixtures |
|  | Power |  |  |  |
|  | HVAC |  |  |  |
|  | Millwork |  |  |  |
|  | Plumbing |  |  |  |
|  | Other |  |  |  |

|  |  |  |  |  |  | DRAFT MAINTENANCE - ARCHITECTURAL INTERIOR PUNCH LIST |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Date Conducted | 2019.01.16 |
|  |  |  | Architect: | BSW |
|  |  |  |  |  | By: | DAchterberg, CCollins, KPhillips, JRonson, CMeredeth, JRichards |
|  |  |  |  | Job No.: | 21607 |
|  | Room No./ Name |  | 3004 MEETING/BREAK |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  |  |
|  | South Wall |  |  |  |  |  |
|  | East Wall |  |  |  |  |  |
|  | West Wall |  |  |  |  | Caulk at floor to frame at storefront. |
|  | Flooring |  |  |  |  |  |
|  | Base |  |  |  |  |  |
|  | Doors |  |  |  |  |  |
|  | Ceiling |  |  |  |  |  |
|  | Lighting |  |  |  |  | Clean can light reflectors |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  | Caulk at counter where existing cable tie penetrates cabinet. Caulk at cabinet base to floor. |
|  | Plumbing |  |  |  |  |  |
|  | Other |  |  |  |  | Install dry erase boards |
|  | Other |  |  |  |  |  |
|  | Room No./ Name |  | 3005 CORRIDOR |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  |  |
|  | South Wall |  |  |  |  |  |
|  | East Wall |  |  |  |  |  |
|  | West Wall |  |  |  |  |  |
|  | Flooring |  |  |  |  |  |
|  | Base |  |  |  |  | Finish base at threshold |
|  |  |  |  |  |  | Extend theshold at doors to walls. Threshold is meant to cover existing recess, not meant to be a traditional threshold. Finish screws in threshold. |
|  | Doors |  |  |  |  | Caulk at threshold to floor. |
|  | Ceiling |  |  |  |  |  |
|  | Lighting |  |  |  |  |  |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  |  |
|  | Plumbing |  |  |  |  |  |
|  | Other |  |  |  |  | Remove angled fire extinguisher sign and patch wall. |
|  | Other |  |  |  |  |  |

|  |  |  |  |  |  | DRAFT MAINTENANCE - ARCHITECTURAL INTERIOR PUNCH LIST |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Date Conducted | 2019.01.16 |
|  |  |  | Architect: | BSW |
|  |  |  |  |  | By: | DAchterberg, CCollins, KPhillips, JRonson, CMeredeth, JRichards |
|  |  |  |  | Job No.: | 21607 |
|  | Room No./ Name |  | 3006 MUD ROOM |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  |  |
|  | South Wall |  |  |  |  |  |
|  | East Wall |  |  |  |  |  |
|  | West Wall |  |  |  |  |  |
|  | Flooring |  |  |  |  |  |
|  | Base |  |  |  |  |  |
|  | Doors |  |  |  |  | Caulk at gap frame to floor (existing floor varies in slope) |
|  | Ceiling |  |  |  |  |  |
|  | Lighting |  |  |  |  | Clean light fixture lens above door |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  |  |
|  | Plumbing |  |  |  |  | Adjust water faucet spout, Caulk around base of mop sink to floor. Add flow labels to piping. |
|  | Other |  |  |  |  |  |
|  | Other |  |  |  |  |  |
|  | Room No./ Name |  | 3007 VESTIBULE |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  | Seal all conduit/pipe/duct penetrations (fire if necessary) |
|  |  |  |  |  |  | At top of wall to equipment, add a steel angle across the length of the wall for ladder support (to service equipment).Seal all conduit/pipe/duct |
|  | South Wall |  |  |  |  | penetrations (fire if necessary) |
|  | East Wall |  |  |  |  | Seal all conduit/pipe/duct penetrations (fire if necessary) |
|  | West Wall |  |  |  |  | Seal all conduit/pipe/duct penetrations (fire if necessary) |
|  | Flooring |  |  |  |  |  |
|  | Base |  |  |  |  |  |
|  |  |  |  |  |  | Door 3007A, repaint, adjust weatherstrip, new door in existing frame, needs adjustment. Door 3001A, caulk at gap frame to floor (existing floor varies |
|  | Doors |  |  |  |  | in slope) |
|  | Ceiling |  |  |  |  |  |
|  | Lighting |  |  |  |  |  |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  |  |
|  | Plumbing |  |  |  |  |  |
|  | Other |  |  |  |  | Check height of fire emergency light AFF, ideally should be lowered to avoid conflict with duct |
|  | Other |  |  |  |  |  |

|  |  |  |  |  |  | DRAFT MAINTENANCE - ARCHITECTURAL INTERIOR PUNCH LIST |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Date Conducted | 2019.01.16 |
|  |  |  | Architect: | BSW |
|  |  |  |  |  | By: | DAchterberg, CCollins, KPhillips, JRonson, CMeredeth, JRichards |
|  |  |  |  | Job No.: | 21607 |
|  | Room No./ Name |  | 3008 MENS SHOWERS |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  | Caulk at top of tile to wall |
|  | South Wall |  |  |  |  | Caulk at top of tile to wall |
|  | East Wall |  |  |  |  | Caulk at top of tile to wall |
|  | West Wall |  |  |  |  | Caulk at top of tile to wall |
|  | Flooring |  |  |  |  |  |
|  | Base |  |  |  |  |  |
|  | Doors |  |  |  |  |  |
|  | Ceiling |  |  |  |  |  |
|  | Lighting |  |  |  |  | Adjust wall mounted light fixture to be straight |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  | Caulk at floor to base, also at seat. |
|  | Plumbing |  |  |  |  | Caulk cleanout under sink. Remove cover and clean out shower trench drain. Adjust shower head to not drip once system is cleaned |
|  | Other |  |  |  |  | Install and towel dispenser and trash can. Install shower curtain and rod. |
|  | Other |  |  |  |  |  |
|  | Room No./ Name |  | 3009 WOMENS SHOWERS |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  | Caulk at top of tile to wall |
|  | South Wall |  |  |  |  | Caulk at top of tile to wall |
|  | East Wall |  |  |  |  | Caulk at top of tile to wall |
|  | West Wall |  |  |  |  | Caulk at top of tile to wall |
|  | Flooring |  |  |  |  |  |
|  | Base |  |  |  |  |  |
|  | Doors |  |  |  |  |  |
|  | Ceiling |  |  |  |  |  |
|  | Lighting |  |  |  |  |  |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  | Caulk at floor to base, also at seat. |
|  | Plumbing |  |  |  |  | Caulk cleanout under sink.Remove cover and clean out trench drain. Adjust shower head to not drip once system is cleaned |
|  | Other |  |  |  |  | Install and towel dispenser and trash can. Install shower curtain and rod. |
|  | Other |  |  |  |  | Fix grab bar escutcheon cover plate. |

|  |  |  |  |  |  | DRAFT MAINTENANCE - ARCHITECTURAL INTERIOR PUNCH LIST |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Date Conducted | 2019.01.16 |
|  |  |  | Architect: | BSW |
|  |  |  |  |  | By: | DAchterberg, CCollins, KPhillips, JRonson, CMeredeth, JRichards |
|  |  |  |  | Job No.: | 21607 |
|  | Room No./ Name |  | 3011 CHEMICAL STORAGE |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  | Caulk at fire, electrical, conduit fixture and switches to fill gaps. |
|  | South Wall |  |  |  |  |  |
|  | East Wall |  |  |  |  |  |
|  | West Wall |  |  |  |  |  |
|  | Flooring |  |  |  |  | Check to see if floors get sealed. |
|  | Base |  |  |  |  |  |
|  | Doors |  |  |  |  | Clean and repaint scratches in doors. |
|  | Ceiling |  |  |  |  | BSW to investigate ceiling options |
|  | Lighting |  |  |  |  |  |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  |  |
|  | Plumbing |  |  |  |  |  |
|  | Other |  |  |  |  | Paint screws on louver grills |
|  | Other |  |  |  |  |  |
|  | Room No./ Name |  | 3012 CHEMICAL STORAGE |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  | Caulk at fire, electrical, conduit fixture and switches to fill gaps. |
|  | South Wall |  |  |  |  |  |
|  | East Wall |  |  |  |  |  |
|  | West Wall |  |  |  |  |  |
|  | Flooring |  |  |  |  | Check to see if floors get sealed. |
|  | Base |  |  |  |  |  |
|  | Doors |  |  |  |  | Clean and repaint scratches in doors. |
|  | Ceiling |  |  |  |  | BSW to investigate ceiling options |
|  | Lighting |  |  |  |  |  |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  |  |
|  | Plumbing |  |  |  |  |  |
|  | Other |  |  |  |  | Paint screws on louver grills |
|  | Other |  |  |  |  |  |

|  |  |  |  |  |  | DRAFT MAINTENANCE - ARCHITECTURAL INTERIOR PUNCH LIST |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Date Conducted | 2019.01.16 |
|  |  |  | Architect: | BSW |
|  |  |  |  |  | By: | DAchterberg, CCollins, KPhillips, JRonson, CMeredeth, JRichards |
|  |  |  |  | Job No.: | 21607 |
|  | Room No./ Name |  | 3013 DATA/IT |
|  | ITEM |  | APP |  | REJ | COMMENTS |
|  | North Wall |  |  |  |  |  |
|  | South Wall |  |  |  |  |  |
|  | East Wall |  |  |  |  |  |
|  | West Wall |  |  |  |  |  |
|  | Flooring |  |  |  |  |  |
|  | Base |  |  |  |  |  |
|  | Doors |  |  |  |  |  |
|  | Ceiling |  |  |  |  |  |
|  | Lighting |  |  |  |  |  |
|  | Power |  |  |  |  |  |
|  | HVAC |  |  |  |  |  |
|  | Millwork |  |  |  |  |  |
|  | Plumbing |  |  |  |  |  |
|  | Other |  |  |  |  | Owner work ongoing. Final clean. |
|  | Other |  |  |  |  |  |